## General
General Data
Slack | 1 | Node slack
Vnom (kV) | 1.32
InternationalSystem | 1 | 1 = International units, 0 = English Units
DeltaLF | 0 | 1 = All loadas are in Delta and the Load Flow is in Delta
V_slack_ph_A | 1.021
V_slack_ph_B | 1.042
V_slack_ph_C | 1.0174
Ang_slack_ph_A | -2.49
Ang_slack_ph_B | -121.72
Ang_slack_ph_C | 117.83

## Topology
Node A | Node B | Length (Km.) | Config.
1 | 3 | 0.05 | 1
1 | 8 | 0.15 | 4
2 | 4 | 0.1 | 5
2 | 7 | 0.15 | 5
3 | 4 | 0.1 | 2
5 | 9 | 0.05 | 1
5 | 10 | 0.1 | 4
6 | 7 | 0.1 | 3
6 | 10 | 0.15 | 4
7 | 8 | 0.15 | 3
7 | 9 | 0.15 | 3

## Configurations
Conf | Lin=1, Trafo=0 | R11 | R12 | R13 | R14 | R22 | R23 | R24 | R33 | R34 | R44 | X11 | X12 | X13 | X14 | X22 | X23 | X24 | X33 | X34 | X44 | B11 | B12 | B13 | B14 | B22 | B23 | B24 | B33 | B34 | B44
1 | 1 | 0.668 | 0 | 0 | 0 | 0.668 | 0 | 0 | 0.668 | 0 | 0.668 | 0.091 | 0.032 | 0.032 | 0.032 | 0.091 | 0.032 | 0.032 | 0.091 | 0.032 | 0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 1.47 | 0 | 0 | 0 | 1.47 | 0 | 0 | 1.47 | 0 | 1.47 | 0.0993 | 0.032 | 0.032 | 0.032 | 0.0993 | 0.032 | 0.032 | 0.0993 | 0.032 | 0.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0.576 | 0 | 0 | 0 | 0.576 | 0 | 0 | 0.576 | 0 | 0.576 | 0.397 | 0.032 | 0.032 | 0.032 | 0.397 | 0.032 | 0.032 | 0.397 | 0.032 | 0.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 0.247 | 0 | 0 | 0 | 0.247 | 0 | 0 | 0.247 | 0 | 0.247 | 0.0833 | 0.032 | 0.032 | 0.032 | 0.0833 | 0.032 | 0.032 | 0.0833 | 0.032 | 0.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 3.93 | 0 | 0 | 0 | 3.93 | 0 | 0 | 3.93 | 0 | 3.93 | 0.113 | 0.032 | 0.032 | 0.032 | 0.113 | 0.032 | 0.032 | 0.113 | 0.032 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 999999999999 | 0 | 0 | 0 | 999999999999 | 0 | 0 | 999999999999 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Loads
Node | Y=1, D=0 | Alfa (PQ=0, I=1, Z=2) | Ph-1 (kW) | Ph-1 (kVAr) | Ph-2 (kW) | Ph-2 (kWAr) | Ph-3 (KW) | Ph-3 (kVAr)
2 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
3 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
4 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
5 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
6 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
7 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
8 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
9 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4
10 | 1 | 1 | 7 | 5.6 | 6 | 4.8 | 5 | 4

## Regulators
Line | Tap A | Tap B | Tap C

## Graphic
Node | Pos X | Pos Y
1 | 0 | 10
7 | 0 | 20
9 | 0 | 30
4 | -10 | 10
5 | -20 | 10
2 | 10 | 10
10 | -10 | 20
6 | -10 | 30
3 | -20 | 20
8 | 20 | 20

## Switches
NODE1 | NODE2 | Closed=1